|  |  | Substation |  |  | {{ substation.name_erms }} |  |  |  |  |  |  |  |  |  |  |  |  | Date: {{ substation.date }} |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | {{ swg.type }} |  | Manufacturer |  |  |  |  |  |  |  |  | {{ swg.manufacturer }} |  | Time: {{ substation.time }} |  |  |  |  |
|  |  | Model |  |  | {{ swg.model }} |  | Rating |  |  |  |  |  |  |  |  | {{ swg.rating }} |  | Humidity: {{ substation.humidity }} |  |  |  |  |
|  |  | Area |  |  | {{ panel.area }} |  |  |  |  |  |  |  |  |  |  | Panel No. |  | {{ panel.linknumber }} |  |  |  |  |
| Panel Name |  | {{ panel.name }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | {{ visual.image }} |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 20.6 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 20.6 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | {{ panel.serialnumber }} |  |  |  |  |
|  | Average Temp. (Ar1) |  | 20.5 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | {{ panel.heateramp }} |  |  |  |  |
|  | Ambient Temp. |  | {{ substation.ambient }} |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | {{ panel.breakerstatus }} |  |  |  |  |
|  | Delta T ( ∆ T) |  | 0.0 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | {{ panel.busbarposition }} |  |  |  |  |
|  | Load (A) |  | {{ panel.loadamp }} |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | {{ panel.cabletype }} |  |  |  |  |
|  | Severity |  | {{ ir.severity }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ULTRASOUND IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | {{ us.prpd }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Decibel (dB) |  |  | {{ us.reading }}dB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound characteristic |  |  | {{ us.char }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Severity |  |  | {{ us.severity }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sound clip |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: {{ analysis }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: {{ recommendation }} |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |