|  |  | Substation |  |  | {{ substation.name_erms }} |  |  |  |  |  |  |  |  |  |  |  | Date: {{ substation.date }} |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | BATTERY BANK |  | Manufacturer |  |  |  |  |  |  | {{ batt.manufacturer }} |  |  | Time: {{ substation.time }} |  |  |  |  |  |  |
|  |  | Model |  |  | {{ batt.model }} |  | Rating |  |  |  |  |  |  | 240V/50Hz |  |  | Humidity: {{ substation.humidity }} |  |  |  |  |  |  |
|  |  | Area |  |  | OVERVIEW |  |  |  |  |  |  |  |  | Battery No. |  |  | {{ batt.number }} |  |  |  |  |  |  |
| Location |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  |  | VALUE |  |  |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | - |  |  |  |  |  |  |  |  |  | Serial No. |  |  |  | {{ batt.serialnumber }} |  |  |  |  |  |  |
|  | Average Temp. (Ar1) |  | 30.0 °C |  |  |  |  |  |  |  |  |  | Heater (A) |  |  |  | - |  |  |  |  |  |  |
|  | Ambient Temp. |  | {{ substation.ambient }} |  |  |  |  |  |  |  |  |  | CB Position |  |  |  | - |  |  |  |  |  |  |
|  | Delta T ( ∆ T) |  | - |  |  |  |  |  |  |  |  |  | Busbar Position |  |  |  | - |  |  |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  | Cable Type |  |  |  | - |  |  |  |  |  |  |
|  | Defect |  | REPAIR IMMEDIATELY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |